# Control narratives, all units

Document number: DOC-CN-001 · Revision C · Issued 2026-03-02 · Owner: Process control engineering

This document describes the function, action, range, tuning and known behaviour of each of the 50 basic control loops of the demonstration refinery (units U-100, U-200, U-300 and U-900). Signals are read from the OPC UA server under CPM.Loops.<loop>.<signal> (PV, SP, OP, MODE). Setpoints and ranges are the values of the plant’s training simulator.

Revision history: Rev. A (2024-05-10) first issue; Rev. B (2025-02-18) tuning after turnaround; Rev. C (2026-03-02) known behaviour notes added for all loops.

## U-100 Crude distillation unit

### FIC-1001 Feed flow

- Unit and area: U-100 Crude distillation unit, Feed

- Equipment: P-1001 Charge pump

- Measurement: FT-1001 (flow, range 0 to 200 m³/h)

- Final element: FV-1001 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality high

- Normal setpoint: 55 m³/h

- Tuning (Rev. C): controller gain 1.1, integral gain 0.12

- Process: time constant about 110 s, dead time about 8 s

Function. FIC-1001 keeps the flow at its setpoint by throttling the control valve FV-1001, on P-1001 Charge pump.

Known behaviour. Performs well. The loop is used as a tuning reference for loops of the same type in this unit.

### FIC-1007 Charge flow

- Unit and area: U-100 Crude distillation unit, Feed

- Equipment: P-1001 Charge pump

- Measurement: FT-1007 (flow, range 0 to 200 m³/h)

- Final element: FV-1007 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 54 m³/h

- Tuning (Rev. C): controller gain 1.25, integral gain 0.18

- Process: time constant about 125 s, dead time about 10 s

Function. FIC-1007 keeps the flow at its setpoint by throttling the control valve FV-1007, on P-1001 Charge pump.

Known behaviour. The setpoint is changed often, by operating campaign and by production targets. Most deviations come from setpoint changes, not from control problems.

Recommended action. Judge this loop on its response to each setpoint change rather than on its variance. See DOC-TG-001, section 4.7.

### TIC-1009 Outlet temperature

- Unit and area: U-100 Crude distillation unit, Heat exchange

- Equipment: E-1009 Feed/product exchanger

- Measurement: TT-1009 (temperature, range 0 to 450 °C)

- Final element: TV-1009 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 60 °C

- Tuning (Rev. C): controller gain 1.3, integral gain 0.16

- Process: time constant about 230 s, dead time about 22 s

Function. TIC-1009 holds the temperature at its setpoint by adjusting the heating or cooling medium valve TV-1009, on E-1009 Feed/product exchanger.

Known behaviour. Recurring load disturbances from upstream changes move the process variable; the loop recovers but each upset takes several minutes.

Recommended action. Consider feedforward from the measured disturbance. Check that the integral action is not too slow. See DOC-TG-001, section 4.8.

### FIC-1101 Column charge flow

- Unit and area: U-100 Crude distillation unit, Distillation

- Equipment: C-1101 Atmospheric column

- Measurement: FT-1101 (flow, range 0 to 200 m³/h)

- Final element: FV-1101 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 63 m³/h

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 105 s, dead time about 15 s

Function. FIC-1101 keeps the flow at its setpoint by throttling the control valve FV-1101, on C-1101 Atmospheric column.

Known behaviour. Performs well. The loop is used as a tuning reference for loops of the same type in this unit.

### FIC-1102 Reflux flow

- Unit and area: U-100 Crude distillation unit, Distillation

- Equipment: P-1102 Reflux pump

- Measurement: FT-1102 (flow, range 0 to 200 m³/h)

- Final element: FV-1102 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 48 m³/h

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 150 s, dead time about 15 s

Function. FIC-1102 keeps the flow at its setpoint by throttling the control valve FV-1102, on P-1102 Reflux pump.

Known behaviour. The control valve shows static friction: the output ramps while the flow stays flat, then the flow jumps. The valve has graphite packing; tightened packing increases friction.

Recommended action. Run a valve travel test (bump the output in manual by 0.5 % steps). If the stem moves only after 2 % or more of output change, schedule packing adjustment or positioner calibration. See DOC-TG-001, section 4.1, and the maintenance history (DOC-MH-001).

### TIC-1104 Furnace temperature

- Unit and area: U-100 Crude distillation unit, Furnaces

- Equipment: F-1104 Atmospheric furnace

- Measurement: TT-1104 (temperature, range 0 to 450 °C)

- Final element: TV-1104 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality high

- Normal setpoint: 68 °C

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 320 s, dead time about 15 s

Function. TIC-1104 holds the temperature at its setpoint by adjusting the heating or cooling medium valve TV-1104, on F-1104 Atmospheric furnace.

Known behaviour. Recurring load disturbances from upstream changes move the process variable; the loop recovers but each upset takes several minutes.

Recommended action. Consider feedforward from the measured disturbance. Check that the integral action is not too slow. See DOC-TG-001, section 4.8.

### LIC-1106 Accumulator level

- Unit and area: U-100 Crude distillation unit, Distillation

- Equipment: D-1106 Overhead accumulator

- Measurement: LT-1106 (level, range 0 to 100 %)

- Final element: LV-1106 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, direct action, criticality medium

- Normal setpoint: 52 %

- Tuning (Rev. C): controller gain 0.68, integral gain 0.05

- Process: time constant about 300 s, dead time about 15 s

Function. LIC-1106 keeps the inventory within the operating band by moving the outlet control valve LV-1106, on D-1106 Overhead accumulator.

Known behaviour. Performs well. The loop is used as a tuning reference for loops of the same type in this unit.

### TIC-1111 Product temperature

- Unit and area: U-100 Crude distillation unit, Heat exchange

- Equipment: E-1009 Feed/product exchanger

- Measurement: TT-1111 (temperature, range 0 to 450 °C)

- Final element: TV-1111 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 61 °C

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 240 s, dead time about 15 s

Function. TIC-1111 holds the temperature at its setpoint by adjusting the heating or cooling medium valve TV-1111, on E-1009 Feed/product exchanger.

Known behaviour. The transmitter or sensing element drifts slowly. Field checks have found offsets of 1 to 3 % of span after several months in service.

Recommended action. Compare with a redundant or portable measurement and recalibrate. Shorten the calibration interval if the drift repeats. See DOC-TG-001, section 4.6.

### FIC-1112 Production flow

- Unit and area: U-100 Crude distillation unit, Feed

- Equipment: P-1001 Charge pump

- Measurement: FT-1112 (flow, range 0 to 200 m³/h)

- Final element: FV-1112 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 56 m³/h

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 150 s, dead time about 15 s

Function. FIC-1112 keeps the flow at its setpoint by throttling the control valve FV-1112, on P-1001 Charge pump.

Known behaviour. The setpoint is changed often, by operating campaign and by production targets. Most deviations come from setpoint changes, not from control problems.

Recommended action. Judge this loop on its response to each setpoint change rather than on its variance. See DOC-TG-001, section 4.7.

### LIC-1113 Reflux drum level

- Unit and area: U-100 Crude distillation unit, Distillation

- Equipment: D-1106 Overhead accumulator

- Measurement: LT-1113 (level, range 0 to 100 %)

- Final element: LV-1113 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, direct action, criticality medium

- Normal setpoint: 84 %

- Tuning (Rev. C): controller gain 1.8, integral gain 0.3

- Process: time constant about 300 s, dead time about 15 s

Function. LIC-1113 keeps the inventory within the operating band by moving the outlet control valve LV-1113, on D-1106 Overhead accumulator.

Known behaviour. The controller output stays at or near its upper limit during high throughput. The valve was sized for the original unit capacity; the capacity increase raised the required flow beyond the valve’s comfortable range.

Recommended action. Check the valve opening against the OP and the hand-wheel position. A valve resize (higher Cv) or a parallel bypass control valve is the permanent fix. See DOC-TG-001, section 4.3.

### TIC-1209 Furnace outlet temperature

- Unit and area: U-100 Crude distillation unit, Furnaces

- Equipment: F-1104 Atmospheric furnace

- Measurement: TT-1209 (temperature, range 0 to 450 °C)

- Final element: TV-1209 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality high

- Normal setpoint: 69 °C

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 340 s, dead time about 15 s

Function. TIC-1209 holds the temperature at its setpoint by adjusting the heating or cooling medium valve TV-1209, on F-1104 Atmospheric furnace.

Known behaviour. The transmitter or sensing element drifts slowly. Field checks have found offsets of 1 to 3 % of span after several months in service.

Recommended action. Compare with a redundant or portable measurement and recalibrate. Shorten the calibration interval if the drift repeats. See DOC-TG-001, section 4.6.

### FIC-1210 Fuel gas flow

- Unit and area: U-100 Crude distillation unit, Furnaces

- Equipment: F-1104 Atmospheric furnace

- Measurement: FT-1210 (flow, range 0 to 200 m³/h)

- Final element: FV-1210 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 57 Nm³/h

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 150 s, dead time about 15 s

Function. FIC-1210 keeps the flow at its setpoint by throttling the control valve FV-1210, on F-1104 Atmospheric furnace.

Known behaviour. The setpoint is changed often, by operating campaign and by production targets. Most deviations come from setpoint changes, not from control problems.

Recommended action. Judge this loop on its response to each setpoint change rather than on its variance. See DOC-TG-001, section 4.7.

### LIC-1211 Flash drum level

- Unit and area: U-100 Crude distillation unit, Distillation

- Equipment: D-1106 Overhead accumulator

- Measurement: LT-1211 (level, range 0 to 100 %)

- Final element: LV-1211 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, direct action, criticality medium

- Normal setpoint: 48 %

- Tuning (Rev. C): controller gain 0.66, integral gain 0.05

- Process: time constant about 310 s, dead time about 15 s

Function. LIC-1211 keeps the inventory within the operating band by moving the outlet control valve LV-1211, on D-1106 Overhead accumulator.

Known behaviour. Recurring load disturbances from upstream changes move the process variable; the loop recovers but each upset takes several minutes.

Recommended action. Consider feedforward from the measured disturbance. Check that the integral action is not too slow. See DOC-TG-001, section 4.8.

### TIC-1213 Column top temperature

- Unit and area: U-100 Crude distillation unit, Distillation

- Equipment: C-1101 Atmospheric column

- Measurement: TT-1213 (temperature, range 0 to 450 °C)

- Final element: TV-1213 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 60 °C

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 235 s, dead time about 15 s

Function. TIC-1213 holds the temperature at its setpoint by adjusting the heating or cooling medium valve TV-1213, on C-1101 Atmospheric column.

Known behaviour. Performs well. The loop is used as a tuning reference for loops of the same type in this unit.

### FIC-1214 Side draw flow

- Unit and area: U-100 Crude distillation unit, Distillation

- Equipment: C-1101 Atmospheric column

- Measurement: FT-1214 (flow, range 0 to 200 m³/h)

- Final element: FV-1214 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 52 m³/h

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 150 s, dead time about 15 s

Function. FIC-1214 keeps the flow at its setpoint by throttling the control valve FV-1214, on C-1101 Atmospheric column.

Known behaviour. The control valve shows static friction: the output ramps while the flow stays flat, then the flow jumps. The valve has graphite packing; tightened packing increases friction.

Recommended action. Run a valve travel test (bump the output in manual by 0.5 % steps). If the stem moves only after 2 % or more of output change, schedule packing adjustment or positioner calibration. See DOC-TG-001, section 4.1, and the maintenance history (DOC-MH-001).

## U-200 Hydrotreating unit

### PIC-1002 Vessel pressure

- Unit and area: U-200 Hydrotreating unit, Separation

- Equipment: V-1004 Product separator

- Measurement: PT-1002 (pressure, range 0 to 100 bar g)

- Final element: PV-1002 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality high

- Normal setpoint: 52 bar

- Tuning (Rev. C): controller gain 2.4, integral gain 0.42

- Process: time constant about 95 s, dead time about 28 s

Function. PIC-1002 holds the pressure at its setpoint by moving the control valve PV-1002, on V-1004 Product separator.

Known behaviour. Persistent cycling with a period of about 3 minutes. The controller gain was raised from 1.6 to 2.4 during the 2025 turnaround to speed recovery after upsets; the cycling started after that change (INC-2026-007).

Recommended action. Reduce the controller gain by about 30 % and repeat a setpoint step test before any valve work. See DOC-TG-001, section 4.2.

### FIC-1003 Recycle flow

- Unit and area: U-200 Hydrotreating unit, Recycle

- Equipment: P-1003 Recycle pump

- Measurement: FT-1003 (flow, range 0 to 200 m³/h)

- Final element: FV-1003 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality high

- Normal setpoint: 58 m³/h

- Tuning (Rev. C): controller gain 1.55, integral gain 0.24

- Process: time constant about 130 s, dead time about 12 s

Function. FIC-1003 keeps the flow at its setpoint by throttling the control valve FV-1003, on P-1003 Recycle pump.

Known behaviour. The control valve FV-1003 shows static friction: the output ramps while the flow stays flat, then the flow jumps. FV-1003 has graphite packing, which was tightened in the last turnaround to stop a stem leak (work order WO-25-1182).

Recommended action. Run a valve travel test (bump the output in manual by 0.5 % steps). If the stem moves only after 2 % or more of output change, schedule packing adjustment or positioner calibration. See DOC-TG-001, section 4.1, and DOC-MH-001.

### LIC-1004 Separator level

- Unit and area: U-200 Hydrotreating unit, Separation

- Equipment: V-1004 Product separator

- Measurement: LT-1004 (level, range 0 to 100 %)

- Final element: LV-1004 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, direct action, criticality medium

- Normal setpoint: 85 %

- Tuning (Rev. C): controller gain 2.1, integral gain 0.38

- Process: time constant about 260 s, dead time about 25 s

Function. LIC-1004 keeps the inventory within the operating band by moving the outlet control valve LV-1004, on V-1004 Product separator.

Known behaviour. The controller output stays at or near its upper limit during high throughput. The valve was sized for the original unit capacity; the capacity increase raised the required flow beyond the valve’s comfortable range.

Recommended action. Check the valve opening against the OP and the hand-wheel position. A valve resize (higher Cv) or a parallel bypass control valve is the permanent fix. See DOC-TG-001, section 4.3.

### TIC-1005 Reactor temperature

- Unit and area: U-200 Hydrotreating unit, Reaction

- Equipment: R-1005 Reactor

- Measurement: TT-1005 (temperature, range 0 to 450 °C)

- Final element: TV-1005 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality high

- Normal setpoint: 62 °C

- Tuning (Rev. C): controller gain 1.4, integral gain 0.15

- Process: time constant about 310 s, dead time about 35 s

Function. TIC-1005 holds the temperature at its setpoint by adjusting the heating or cooling medium valve TV-1005, on R-1005 Reactor.

Known behaviour. The loop spends long periods in manual mode. Operators switch it to manual during feed changes since an overshoot event in 2025 (INC-2025-031). It was retuned after that event.

Recommended action. Agree an automatic-mode target with operations and watch the first feed changes in automatic. See DOC-TG-001, section 4.4.

### AIC-1006 Product composition

- Unit and area: U-200 Hydrotreating unit, Quality

- Equipment: u-200-quality Quality

- Measurement: AT-1006 (composition, range 0 to 100 %)

- Final element: AV-1006 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 50 mol%

- Tuning (Rev. C): controller gain 1.05, integral gain 0.11

- Process: time constant about 180 s, dead time about 18 s

Function. AIC-1006 holds the analyzed composition at its setpoint by trimming the manipulated stream AV-1006, on u-200-quality Quality.

Known behaviour. The measurement carries high-frequency noise from the analyzer sample system. The controller passes the noise to the valve and wears the actuator.

Recommended action. Check the sample conditioning system (filters, sample flow, lag time) and set a first-order PV filter of 5 to 10 seconds. See DOC-TG-001, section 4.5.

### LIC-1010 Interface level

- Unit and area: U-200 Hydrotreating unit, Separation

- Equipment: V-1004 Product separator

- Measurement: LT-1010 (level, range 0 to 100 %)

- Final element: LV-1010 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, direct action, criticality medium

- Normal setpoint: 51 %

- Tuning (Rev. C): controller gain 1.15, integral gain 0.13

- Process: time constant about 190 s, dead time about 20 s

Function. LIC-1010 keeps the inventory within the operating band by moving the outlet control valve LV-1010, on V-1004 Product separator.

Known behaviour. The loop interacts with a neighbouring stream (the SECONDARY signal on the OPC UA server): moves in one disturb the other.

Recommended action. Tune the two loops at different speeds (the faster loop at least three times faster) or add decoupling. See DOC-TG-001, section 4.9.

Interaction. The OPC UA server also publishes CPM.Loops.LIC-1010.SECONDARY, the flow of the neighbouring stream that interacts with this loop.

### PIC-1103 Suction pressure

- Unit and area: U-200 Hydrotreating unit, Compression

- Equipment: K-1103 Recycle gas compressor

- Measurement: PT-1103 (pressure, range 0 to 100 bar g)

- Final element: PV-1103 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality high

- Normal setpoint: 46 bar

- Tuning (Rev. C): controller gain 2.2, integral gain 0.38

- Process: time constant about 150 s, dead time about 26 s

Function. PIC-1103 holds the pressure at its setpoint by moving the control valve PV-1103, on K-1103 Recycle gas compressor.

Known behaviour. Persistent cycling with a period of 2 to 4 minutes has been reported. The controller gain was raised during the last turnaround to speed recovery after upsets; the cycling started after that change.

Recommended action. Reduce the controller gain by about 30 % and repeat a setpoint step test before any valve work. See the Control Loop Troubleshooting Guide (DOC-TG-001), section 4.2.

### LIC-1105 Surge drum level

- Unit and area: U-200 Hydrotreating unit, Separation

- Equipment: V-1105 Surge drum

- Measurement: LT-1105 (level, range 0 to 100 %)

- Final element: LV-1105 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, direct action, criticality medium

- Normal setpoint: 50 %

- Tuning (Rev. C): controller gain 0.72, integral gain 0.06

- Process: time constant about 280 s, dead time about 15 s

Function. LIC-1105 keeps the inventory within the operating band by moving the outlet control valve LV-1105, on V-1105 Surge drum.

Known behaviour. Recurring load disturbances from upstream changes move the process variable; the loop recovers but each upset takes several minutes.

Recommended action. Consider feedforward from the measured disturbance. Check that the integral action is not too slow. See DOC-TG-001, section 4.8.

### AIC-1108 Stream composition

- Unit and area: U-200 Hydrotreating unit, Quality

- Equipment: u-200-quality Quality

- Measurement: AT-1108 (composition, range 0 to 100 %)

- Final element: AV-1108 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 55 mol%

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 150 s, dead time about 15 s

Function. AIC-1108 holds the analyzed composition at its setpoint by trimming the manipulated stream AV-1108, on u-200-quality Quality.

Known behaviour. The measurement carries high-frequency noise from the analyzer sample system. The controller passes the noise to the valve and wears the actuator.

Recommended action. Check the sample conditioning system (filters, sample flow, lag time) and set a first-order PV filter of 5 to 10 seconds. See DOC-TG-001, section 4.5.

### FIC-1201 Hydrotreater charge flow

- Unit and area: U-200 Hydrotreating unit, Hydrotreating

- Equipment: R-1203 Hydrotreating reactor

- Measurement: FT-1201 (flow, range 0 to 200 m³/h)

- Final element: FV-1201 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 64 m³/h

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 115 s, dead time about 15 s

Function. FIC-1201 keeps the flow at its setpoint by throttling the control valve FV-1201, on R-1203 Hydrotreating reactor.

Known behaviour. Performs well. The loop is used as a tuning reference for loops of the same type in this unit.

### PIC-1202 Reactor inlet pressure

- Unit and area: U-200 Hydrotreating unit, Hydrotreating

- Equipment: R-1203 Hydrotreating reactor

- Measurement: PT-1202 (pressure, range 0 to 100 bar g)

- Final element: PV-1202 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality high

- Normal setpoint: 56 bar

- Tuning (Rev. C): controller gain 2.25, integral gain 0.39

- Process: time constant about 150 s, dead time about 27 s

Function. PIC-1202 holds the pressure at its setpoint by moving the control valve PV-1202, on R-1203 Hydrotreating reactor.

Known behaviour. Persistent cycling with a period of 2 to 4 minutes has been reported. The controller gain was raised during the last turnaround to speed recovery after upsets; the cycling started after that change.

Recommended action. Reduce the controller gain by about 30 % and repeat a setpoint step test before any valve work. See the Control Loop Troubleshooting Guide (DOC-TG-001), section 4.2.

### TIC-1203 Catalyst bed temperature

- Unit and area: U-200 Hydrotreating unit, Hydrotreating

- Equipment: R-1203 Hydrotreating reactor

- Measurement: TT-1203 (temperature, range 0 to 450 °C)

- Final element: TV-1203 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality high

- Normal setpoint: 66 °C

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 330 s, dead time about 15 s

Function. TIC-1203 holds the temperature at its setpoint by adjusting the heating or cooling medium valve TV-1203, on R-1203 Hydrotreating reactor.

Known behaviour. Recurring load disturbances from upstream changes move the process variable; the loop recovers but each upset takes several minutes.

Recommended action. Consider feedforward from the measured disturbance. Check that the integral action is not too slow. See DOC-TG-001, section 4.8.

### LIC-1204 High-pressure separator level

- Unit and area: U-200 Hydrotreating unit, Hydrotreating

- Equipment: V-1204 High-pressure separator

- Measurement: LT-1204 (level, range 0 to 100 %)

- Final element: LV-1204 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, direct action, criticality medium

- Normal setpoint: 51 %

- Tuning (Rev. C): controller gain 0.7, integral gain 0.05

- Process: time constant about 290 s, dead time about 15 s

Function. LIC-1204 keeps the inventory within the operating band by moving the outlet control valve LV-1204, on V-1204 High-pressure separator.

Known behaviour. Performs well. The loop is used as a tuning reference for loops of the same type in this unit.

### AIC-1205 Hydrogen purity

- Unit and area: U-200 Hydrotreating unit, Hydrotreating

- Equipment: V-1204 High-pressure separator

- Measurement: AT-1205 (composition, range 0 to 100 %)

- Final element: AV-1205 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 58 mol%

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 150 s, dead time about 15 s

Function. AIC-1205 holds the analyzed composition at its setpoint by trimming the manipulated stream AV-1205, on V-1204 High-pressure separator.

Known behaviour. The measurement carries high-frequency noise from the analyzer sample system. The controller passes the noise to the valve and wears the actuator.

Recommended action. Check the sample conditioning system (filters, sample flow, lag time) and set a first-order PV filter of 5 to 10 seconds. See DOC-TG-001, section 4.5.

### FIC-1206 Quench flow

- Unit and area: U-200 Hydrotreating unit, Hydrotreating

- Equipment: R-1203 Hydrotreating reactor

- Measurement: FT-1206 (flow, range 0 to 200 m³/h)

- Final element: FV-1206 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 47 m³/h

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 150 s, dead time about 15 s

Function. FIC-1206 keeps the flow at its setpoint by throttling the control valve FV-1206, on R-1203 Hydrotreating reactor.

Known behaviour. The control valve shows static friction: the output ramps while the flow stays flat, then the flow jumps. The valve has graphite packing; tightened packing increases friction.

Recommended action. Run a valve travel test (bump the output in manual by 0.5 % steps). If the stem moves only after 2 % or more of output change, schedule packing adjustment or positioner calibration. See DOC-TG-001, section 4.1, and the maintenance history (DOC-MH-001).

### PIC-1207 Compressor discharge pressure

- Unit and area: U-200 Hydrotreating unit, Compression

- Equipment: K-1103 Recycle gas compressor

- Measurement: PT-1207 (pressure, range 0 to 100 bar g)

- Final element: PV-1207 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 83 bar

- Tuning (Rev. C): controller gain 2.05, integral gain 0.35

- Process: time constant about 150 s, dead time about 15 s

Function. PIC-1207 holds the pressure at its setpoint by moving the control valve PV-1207, on K-1103 Recycle gas compressor.

Known behaviour. The controller output stays at or near its upper limit during high throughput. The valve was sized for the original unit capacity; the capacity increase raised the required flow beyond the valve’s comfortable range.

Recommended action. Check the valve opening against the OP and the hand-wheel position. A valve resize (higher Cv) or a parallel bypass control valve is the permanent fix. See DOC-TG-001, section 4.3.

### LIC-1208 Suction drum level

- Unit and area: U-200 Hydrotreating unit, Compression

- Equipment: V-1208 Compressor suction drum

- Measurement: LT-1208 (level, range 0 to 100 %)

- Final element: LV-1208 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, direct action, criticality medium

- Normal setpoint: 50 %

- Tuning (Rev. C): controller gain 0.72, integral gain 0.06

- Process: time constant about 275 s, dead time about 15 s

Function. LIC-1208 keeps the inventory within the operating band by moving the outlet control valve LV-1208, on V-1208 Compressor suction drum.

Known behaviour. The loop interacts with a neighbouring stream (the SECONDARY signal on the OPC UA server): moves in one disturb the other.

Recommended action. Tune the two loops at different speeds (the faster loop at least three times faster) or add decoupling. See DOC-TG-001, section 4.9.

Interaction. The OPC UA server also publishes CPM.Loops.LIC-1208.SECONDARY, the flow of the neighbouring stream that interacts with this loop.

### AIC-1215 Sulfur content in product

- Unit and area: U-200 Hydrotreating unit, Quality

- Equipment: u-200-quality Quality

- Measurement: AT-1215 (composition, range 0 to 100 %)

- Final element: AV-1215 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 45 ppm

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 150 s, dead time about 15 s

Function. AIC-1215 holds the analyzed composition at its setpoint by trimming the manipulated stream AV-1215, on u-200-quality Quality.

Known behaviour. The measurement carries high-frequency noise from the analyzer sample system. The controller passes the noise to the valve and wears the actuator.

Recommended action. Check the sample conditioning system (filters, sample flow, lag time) and set a first-order PV filter of 5 to 10 seconds. See DOC-TG-001, section 4.5.

## U-300 Treating and sulfur recovery

### LIC-1107 Interface level (treating)

- Unit and area: U-300 Treating and sulfur recovery, Treating

- Equipment: C-1216 Amine absorber

- Measurement: LT-1107 (level, range 0 to 100 %)

- Final element: LV-1107 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, direct action, criticality medium

- Normal setpoint: 49 %

- Tuning (Rev. C): controller gain 0.75, integral gain 0.06

- Process: time constant about 260 s, dead time about 15 s

Function. LIC-1107 keeps the inventory within the operating band by moving the outlet control valve LV-1107, on C-1216 Amine absorber.

Known behaviour. The loop interacts with a neighbouring stream (the SECONDARY signal on the OPC UA server): moves in one disturb the other.

Recommended action. Tune the two loops at different speeds (the faster loop at least three times faster) or add decoupling. See DOC-TG-001, section 4.9.

Interaction. The OPC UA server also publishes CPM.Loops.LIC-1107.SECONDARY, the flow of the neighbouring stream that interacts with this loop.

### TIC-1114 Stabilizer temperature

- Unit and area: U-300 Treating and sulfur recovery, Treating

- Equipment: C-1216 Amine absorber

- Measurement: TT-1114 (temperature, range 0 to 450 °C)

- Final element: TV-1114 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 59 °C

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 210 s, dead time about 15 s

Function. TIC-1114 holds the temperature at its setpoint by adjusting the heating or cooling medium valve TV-1114, on C-1216 Amine absorber.

Known behaviour. Performs well. The loop is used as a tuning reference for loops of the same type in this unit.

### LIC-1216 Amine absorber level

- Unit and area: U-300 Treating and sulfur recovery, Treating

- Equipment: C-1216 Amine absorber

- Measurement: LT-1216 (level, range 0 to 100 %)

- Final element: LV-1216 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, direct action, criticality medium

- Normal setpoint: 54 %

- Tuning (Rev. C): controller gain 0.68, integral gain 0.05

- Process: time constant about 305 s, dead time about 15 s

Function. LIC-1216 keeps the inventory within the operating band by moving the outlet control valve LV-1216, on C-1216 Amine absorber.

Known behaviour. Performs well. The loop is used as a tuning reference for loops of the same type in this unit.

### TIC-1226 Sulfur reactor temperature

- Unit and area: U-300 Treating and sulfur recovery, Sulfur recovery

- Equipment: R-1226 Claus reactor

- Measurement: TT-1226 (temperature, range 0 to 450 °C)

- Final element: TV-1226 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality medium

- Normal setpoint: 67 °C

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 315 s, dead time about 15 s

Function. TIC-1226 holds the temperature at its setpoint by adjusting the heating or cooling medium valve TV-1226, on R-1226 Claus reactor.

Known behaviour. Recurring load disturbances from upstream changes move the process variable; the loop recovers but each upset takes several minutes.

Recommended action. Consider feedforward from the measured disturbance. Check that the integral action is not too slow. See DOC-TG-001, section 4.8.

## U-900 Utilities and offsites

### PIC-1008 Header pressure

- Unit and area: U-900 Utilities and offsites, Utilities

- Equipment: u-900-utilities Utilities

- Measurement: PT-1008 (pressure, range 0 to 100 bar g)

- Final element: PV-1008 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality low

- Normal setpoint: 57 bar

- Tuning (Rev. C): controller gain 1.1, integral gain 0.12

- Process: time constant about 165 s, dead time about 14 s

Function. PIC-1008 holds the pressure at its setpoint by moving the control valve PV-1008, on u-900-utilities Utilities.

Known behaviour. The transmitter or sensing element drifts slowly. Field checks have found offsets of 1 to 3 % of span after several months in service.

Recommended action. Compare with a redundant or portable measurement and recalibrate. Shorten the calibration interval if the drift repeats. See DOC-TG-001, section 4.6.

### FIC-1109 Steam flow

- Unit and area: U-900 Utilities and offsites, Utilities

- Equipment: V-1218 Condensate drum

- Measurement: FT-1109 (flow, range 0 to 200 m³/h)

- Final element: FV-1109 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality low

- Normal setpoint: 82 t/h

- Tuning (Rev. C): controller gain 2, integral gain 0.34

- Process: time constant about 150 s, dead time about 15 s

Function. FIC-1109 keeps the flow at its setpoint by throttling the control valve FV-1109, on V-1218 Condensate drum.

Known behaviour. The controller output stays at or near its upper limit during high throughput. The valve was sized for the original unit capacity; the capacity increase raised the required flow beyond the valve’s comfortable range.

Recommended action. Check the valve opening against the OP and the hand-wheel position. A valve resize (higher Cv) or a parallel bypass control valve is the permanent fix. See DOC-TG-001, section 4.3.

### PIC-1110 Network pressure

- Unit and area: U-900 Utilities and offsites, Utilities

- Equipment: u-900-utilities Utilities

- Measurement: PT-1110 (pressure, range 0 to 100 bar g)

- Final element: PV-1110 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality low

- Normal setpoint: 58 bar

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 150 s, dead time about 15 s

Function. PIC-1110 holds the pressure at its setpoint by moving the control valve PV-1110, on u-900-utilities Utilities.

Known behaviour. The loop spends long periods in manual mode. Operators switch it to manual during transients because of past erratic behaviour.

Recommended action. Find why the operators distrust the loop (shift log, interviews), fix that cause, retune, and agree an automatic-mode target with operations. See DOC-TG-001, section 4.4.

### PIC-1212 Flare header pressure

- Unit and area: U-900 Utilities and offsites, Utilities

- Equipment: u-900-utilities Utilities

- Measurement: PT-1212 (pressure, range 0 to 100 bar g)

- Final element: PV-1212 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality low

- Normal setpoint: 53 bar

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 150 s, dead time about 15 s

Function. PIC-1212 holds the pressure at its setpoint by moving the control valve PV-1212, on u-900-utilities Utilities.

Known behaviour. The loop spends long periods in manual mode. Operators switch it to manual during transients because of past erratic behaviour.

Recommended action. Find why the operators distrust the loop (shift log, interviews), fix that cause, retune, and agree an automatic-mode target with operations. See DOC-TG-001, section 4.4.

### PIC-1217 Medium-pressure steam pressure

- Unit and area: U-900 Utilities and offsites, Utilities

- Equipment: V-1218 Condensate drum

- Measurement: PT-1217 (pressure, range 0 to 100 bar g)

- Final element: PV-1217 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality low

- Normal setpoint: 62 bar

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 175 s, dead time about 15 s

Function. PIC-1217 holds the pressure at its setpoint by moving the control valve PV-1217, on V-1218 Condensate drum.

Known behaviour. Recurring load disturbances from upstream changes move the process variable; the loop recovers but each upset takes several minutes.

Recommended action. Consider feedforward from the measured disturbance. Check that the integral action is not too slow. See DOC-TG-001, section 4.8.

### LIC-1218 Condensate drum level

- Unit and area: U-900 Utilities and offsites, Utilities

- Equipment: V-1218 Condensate drum

- Measurement: LT-1218 (level, range 0 to 100 %)

- Final element: LV-1218 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, direct action, criticality low

- Normal setpoint: 50 %

- Tuning (Rev. C): controller gain 0.7, integral gain 0.05

- Process: time constant about 285 s, dead time about 15 s

Function. LIC-1218 keeps the inventory within the operating band by moving the outlet control valve LV-1218, on V-1218 Condensate drum.

Known behaviour. The loop interacts with a neighbouring stream (the SECONDARY signal on the OPC UA server): moves in one disturb the other.

Recommended action. Tune the two loops at different speeds (the faster loop at least three times faster) or add decoupling. See DOC-TG-001, section 4.9.

Interaction. The OPC UA server also publishes CPM.Loops.LIC-1218.SECONDARY, the flow of the neighbouring stream that interacts with this loop.

### FIC-1219 Cooling water flow

- Unit and area: U-900 Utilities and offsites, Utilities

- Equipment: P-1219 Cooling water pump

- Measurement: FT-1219 (flow, range 0 to 200 m³/h)

- Final element: FV-1219 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality low

- Normal setpoint: 81 m³/h

- Tuning (Rev. C): controller gain 1.95, integral gain 0.33

- Process: time constant about 150 s, dead time about 15 s

Function. FIC-1219 keeps the flow at its setpoint by throttling the control valve FV-1219, on P-1219 Cooling water pump.

Known behaviour. The controller output stays at or near its upper limit during high throughput. The valve was sized for the original unit capacity; the capacity increase raised the required flow beyond the valve’s comfortable range.

Recommended action. Check the valve opening against the OP and the hand-wheel position. A valve resize (higher Cv) or a parallel bypass control valve is the permanent fix. See DOC-TG-001, section 4.3.

### TIC-1220 Water return temperature

- Unit and area: U-900 Utilities and offsites, Utilities

- Equipment: P-1219 Cooling water pump

- Measurement: TT-1220 (temperature, range 0 to 450 °C)

- Final element: TV-1220 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality low

- Normal setpoint: 55 °C

- Tuning (Rev. C): controller gain 2.15, integral gain 0.36

- Process: time constant about 150 s, dead time about 25 s

Function. TIC-1220 holds the temperature at its setpoint by adjusting the heating or cooling medium valve TV-1220, on P-1219 Cooling water pump.

Known behaviour. The return temperature cycles because the consumers’ own temperature loops act on the same cooling water (interaction with consumers), not because of its own tuning.

Recommended action. Check the large consumers’ temperature loops before retuning TIC-1220. See DOC-TG-001, section 4.2, and DOC-U900-OM-001, section 3.

### PIC-1221 Nitrogen network pressure

- Unit and area: U-900 Utilities and offsites, Utilities

- Equipment: u-900-utilities Utilities

- Measurement: PT-1221 (pressure, range 0 to 100 bar g)

- Final element: PV-1221 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality low

- Normal setpoint: 57 bar

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 155 s, dead time about 15 s

Function. PIC-1221 holds the pressure at its setpoint by moving the control valve PV-1221, on u-900-utilities Utilities.

Known behaviour. Performs well. The loop is used as a tuning reference for loops of the same type in this unit.

### FIC-1222 Effluent flow to treatment

- Unit and area: U-900 Utilities and offsites, Water treatment

- Equipment: TK-1223 Equalization tank

- Measurement: FT-1222 (flow, range 0 to 200 m³/h)

- Final element: FV-1222 (equal percentage characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality low

- Normal setpoint: 49 m³/h

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 150 s, dead time about 15 s

Function. FIC-1222 keeps the flow at its setpoint by throttling the control valve FV-1222, on TK-1223 Equalization tank.

Known behaviour. The setpoint is changed often, by operating campaign and by production targets. Most deviations come from setpoint changes, not from control problems.

Recommended action. Judge this loop on its response to each setpoint change rather than on its variance. See DOC-TG-001, section 4.7.

### LIC-1223 Equalization tank level

- Unit and area: U-900 Utilities and offsites, Water treatment

- Equipment: TK-1223 Equalization tank

- Measurement: LT-1223 (level, range 0 to 100 %)

- Final element: LV-1223 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, direct action, criticality low

- Normal setpoint: 52 %

- Tuning (Rev. C): controller gain 0.65, integral gain 0.05

- Process: time constant about 325 s, dead time about 15 s

Function. LIC-1223 keeps the inventory within the operating band by moving the outlet control valve LV-1223, on TK-1223 Equalization tank.

Known behaviour. The loop spends long periods in manual mode. Operators switch it to manual during transients because of past erratic behaviour.

Recommended action. Find why the operators distrust the loop (shift log, interviews), fix that cause, retune, and agree an automatic-mode target with operations. See DOC-TG-001, section 4.4.

### AIC-1224 Treated effluent pH

- Unit and area: U-900 Utilities and offsites, Water treatment

- Equipment: TK-1223 Equalization tank

- Measurement: AT-1224 (composition, range 0 to 100 % of analyzer span (0 to 14 pH))

- Final element: AV-1224 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, reverse action, criticality low

- Normal setpoint: 50 % of span (pH 7.0)

- Tuning (Rev. C): controller gain 1.25, integral gain 0.16

- Process: time constant about 195 s, dead time about 15 s

Function. AIC-1224 holds the analyzed composition at its setpoint by trimming the manipulated stream AV-1224, on TK-1223 Equalization tank.

Known behaviour. The transmitter or sensing element drifts slowly. Field checks have found offsets of 1 to 3 % of span after several months in service.

Recommended action. Compare with a redundant or portable measurement and recalibrate. Shorten the calibration interval if the drift repeats. See DOC-TG-001, section 4.6.

### LIC-1225 Slop tank level

- Unit and area: U-900 Utilities and offsites, Water treatment

- Equipment: TK-1225 Slop tank

- Measurement: LT-1225 (level, range 0 to 100 %)

- Final element: LV-1225 (linear characteristic, pneumatic actuator)

- Controller: PID in the DCS, direct action, criticality low

- Normal setpoint: 47 %

- Tuning (Rev. C): controller gain 0.64, integral gain 0.05

- Process: time constant about 320 s, dead time about 15 s

Function. LIC-1225 keeps the inventory within the operating band by moving the outlet control valve LV-1225, on TK-1225 Slop tank.

Known behaviour. The loop interacts with a neighbouring stream (the SECONDARY signal on the OPC UA server): moves in one disturb the other.

Recommended action. Tune the two loops at different speeds (the faster loop at least three times faster) or add decoupling. See DOC-TG-001, section 4.9.

Interaction. The OPC UA server also publishes CPM.Loops.LIC-1225.SECONDARY, the flow of the neighbouring stream that interacts with this loop.